## Slide 1: Multi-Period Optimization for Power Distribution Systems with Battery Storage
Aryan Ritwajeet Jha
Notes: Remember to hit the reset button to make sure all the page elements react properly.
There are 20 different layouts that you can choose from.

## Slide 2: Optimal Multi-Period Dispatch of Distributed Energy Resources in Unbalanced Distribution Feeders
Nawaf Nazir, Pavan Racherla and Mads Almassalkhi
IEEE TRANSACTIONS IN POWER SYSTEMS (2020)
Currently at PNNL PhD at University of Vermont (UVM)
Currently Asst. Prof. at UVM
Currently Assoc. Prof. at UVM

## Slide 3: Optimal Multi-Period Dispatch of Distributed Energy Resources in Unbalanced Distribution Feeders
Distribution System
  Unbalanced
  Inverter-Interfaced
  Significant Solar Penetration
Three-Phase Unbalanced
  Non-Convex Loss-minimization problem
  Formulated as a Convex Second Order Conic Program (SOCP) for arriving at an initial solution for Non-Linear Program (NLP)
  NLP run to ensure physically realizable solution

## Slide 4: Optimal Multi-Period Dispatch of Distributed Energy Resources in Unbalanced Distribution Feeders
Conditions derived to ensure that batteries do NOT simultaneously charge and discharge. (Is that a big problem?)
Tested with GridLab-D for IEEE 13 and IEEE 123.
  AC feasibility of the solutions ensured
  Near-optimal performance
  Solution time < 1 min.

## Slide 5: Optimal Multi-Period Dispatch of Distributed Energy Resources in Unbalanced Distribution Feeders
ConEd* of NY moving towards Distributed System Platforms (DSPs)
These DSPs allow for DERs to be factored into Optimization schemes for Power Generation
DERs can be Optimized to function as Virtual Batteries (VBs)
  provide energy services at different spatio-temporal scales.
* Consolidated Edison, electric utility in NY and NOT ComEd, Commonwealth Edison, electric utility in IL

## Slide 6: Optimal Multi-Period Dispatch of Distributed Energy Resources in Unbalanced Distribution Feeders
  Traditionally, DistFlow algorithms based on the Branch Flow Model (BFM), which are an exact non-linear formulation of the distribution power flow equations, only work on balanced single-phase equivalent networks.
  But Distribution Networks are inherently unbalanced.

## Slide 7: Optimal Multi-Period Dispatch of Distributed Energy Resources in Unbalanced Distribution Feeders
  In [22] by the same authors, they have developed a three-phase convex SOCP relaxation of the multi-period OPF problem, and provided sufficient conditions which ensure the avoidance of simultaneous charging and discharging.
  In this paper, they extend the work by developing a Multi-Period SOCP-NLP algorithm that provides a near optimal and guaranteed feasible solution.

## Slide 8: Optimal Multi-Period Dispatch of Distributed Energy Resources in Unbalanced Distribution Feeders
  The optimized solutions from the relaxed SOCP model, are used to initialize a Non-Linear Program (NLP) of the actual AC Power Flow, to obtain a physically realizable solution.
  Real-Power Solutions that form the energy trajectory and are obtained from the SOCP, are fixed in the NLP, leading to a decoupling of the different time-steps. (What? How?)
  As a result, the NLP solves for each time-step separately (possibly in-parallel), leading to a scalable framework. (What?)
  Validation is performed using GridLab-D.

## Slide 9: Optimal Multi-Period Dispatch of Distributed Energy Resources in Unbalanced Distribution Feeders
  Case Study Description
  IEEE , Unbalanced,
  Algorithm implemented in Receding-Horizon fashion.
  Receding-Horizon means a rolling window where predictions for the next time-steps from time to are made at time and since predictions are updated at every time step, for the next time step , predictions for the next time steps from to are once again made.
  The cycle goes on.
Fig. Aggregate solar, demand and net-demand profile over a prediction horizon of

## Slide 10: Optimal Multi-Period Dispatch of Distributed Energy Resources in Unbalanced Distribution Feeders
The SOCP solution outputs an optimal battery and inverter control schedule
The schedule is used by the NLP to calculate a physically realizable schedule
The physically realizable schedule is implemented by GridLab-D to determine the resulting AC Power Flows.
The forecast of demand and renewable generations are updated.
The Process

## Slide 11: Optimal Multi-Period Dispatch of Distributed Energy Resources in Unbalanced Distribution Feeders
The Process
Fig. Coupling of SOCP with NLP by fixing real power solutions from SOCP and hence decoupling the NLP to obtain a feasible solution. (What? How?)
Fig. Available reactive power variation range for NLP across multiple time-steps based on the active power trajectory provided by the SOCP.

## Slide 12: Optimal Multi-Period Dispatch of Distributed Energy Resources in Unbalanced Distribution Feeders
  Case Study Description
  Distributed Storage and Solar PV Units randomly added to nodes
    They can supply active and reactive power through four quadrant operation.
    Each storage unit has capacity and apparent power rating
    Each solar PV unit has a rating
  Solar and Load Profile prediction horizon
    Each step

## Slide 13: Optimal Multi-Period Dispatch of Distributed Energy Resources in Unbalanced Distribution Feeders
  Case Study Description
  Three-phase OPF is run in a receding horizon fashion with prediction horizon of time-steps, for the dispatch of controllable assets of the network to minimize network losses.
  Set-points provided by the solutions of the SOCP are used to initialize an NLP to provide a feasible solution.
    SOCP modeled in JuMP, with Julia and solved using GUROBI.
      Multi-period SOCP has
        kvariables (k as in thousand)
        k linear constraints
        k SOC constraints

## Slide 14: Optimal Multi-Period Dispatch of Distributed Energy Resources in Unbalanced Distribution Feeders
  Case Study Description
    NLP also modeled in JuMP, but solved using IPOPT [36] using the HSL_MA86 solver [37]
      A single-period of the Multi-period SOCP has
        kvariables
        k linear constraints
        k SOC constraints
        k non-linear constraints

## Slide 15: Optimal Multi-Period Dispatch of Distributed Energy Resources in Unbalanced Distribution Feeders
  Results
    levels for both loads (low and high) and solar PV generation (low and high)
    ‘High’ implies Base Values for both Loads as well as solar PV
    ‘Low’ implies of the base values in both cases.
    Thus scenarios are modeled:
      LL (Low Solar, Low Loads)
      LH (Low Solar, High Loads)
      HL (High Solar, Low Loads)
      HH (High Solar, High Loads)
Different Solar and Load Cases

## Slide 16: Optimal Multi-Period Dispatch of Distributed Energy Resources in Unbalanced Distribution Feeders
  Results
  Optimality gap always below 3% for different solar penetration levels.
  Feasible solutions always ( difference).
  Solution times
  NLP total time assuming parallelized operation over every single time step.
Table: Comparison of the Optimality Gap Values of SOCP and NLP.

## Slide 17: References
[22] Nazir, N., & Almassalkhi, M. (2018). Receding-Horizon Optimization of Unbalanced Distribution Systems with Time-Scale Separation for Discrete and Continuous Control Devices. 2018 Power Systems Computation Conference (PSCC). IEEE. doi: 10.23919/PSCC.2018.8442555
[36] Wächter, A., & Biegler, L. T. (2006). On the implementation of an interior-point filter line-search algorithm for large-scale nonlinear programming. Math. Program., 106(1), 25–57. doi: 10.1007/s10107-004-0559-y
[37] HSL - Home Page. (2023, May 24). Retrieved from https://www.hsl.rl.ac.uk